{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"1","index":0,"n_rows":136,"n_cols":44,"rows_kept":136,"flags":["formulas_cached_only"]}
["所属设备","测点名称","测点描述","测点类型","读写属性","系数K","偏移B","初始值","数值转换","原始值","转换后的值","测点分组","采集类型码","寄存器地址","数据类型","数据格式","按位取值","起始位","终止位","报警使能","历史存储使能","高高报警使能","高报警使能","低报警使能","低低报警使能","高高报警限值","高报警限值","低报警限值","低低报警限值","高高报消息","高报消息","低报消息","低低报消息","报警死区","开关报警","开关报警消息","报警级别","存储方式","存储间隔(秒)","压缩精度","是否上传","PV上传标识","辅助参数","Reserve2"]
["阳光逆变器","RF","daypositiveActice","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5002","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","238","0","0"]
["阳光逆变器","ZF","positiveActice","模拟量","读写","1.0","0.0","0.0","0","512","0","0","4","5003","32位无符号","3412","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","240","0","0"]
["阳光逆变器","RUNT","opentime","模拟量","读写","1.0","0.0","0.0","0","512","0","0","4","5005","32位无符号","3412","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","Temp","temperature","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5007","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","36","0","0"]
["阳光逆变器","Pdc","inputep","模拟量","读写","0.001","0.0","0.0","0","512","0","0","4","5016","32位无符号","3412","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","60","0.5","1","164","0","0"]
["阳光逆变器","Ua","ua","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5018","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","9","0","0"]
["阳光逆变器","Ub","ub","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5019","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","10","0","0"]
["阳光逆变器","Uc","uc","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5020","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","11","0","0"]
["阳光逆变器","Ia","ia","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5021","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","0","0","0"]
["阳光逆变器","Ib","ib","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5022","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","1","0","0"]
["阳光逆变器","Ic","ic","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5023","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","2","0","0"]
["阳光逆变器","Pac","ep","模拟量","读写","0.001","0.0","0.0","0","512","0","0","4","5030","32位无符号","3412","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","17","0","0"]
["阳光逆变器","S","s","模拟量","读写","0.001","0.0","0.0","0","512","0","0","4","5030","32位无符号","3412","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","16","0","0"]
["阳光逆变器","Q","eq","模拟量","读写","0.001","0.0","0.0","0","512","0","0","4","5032","32位有符号","3412","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","18","0","0"]
["阳光逆变器","COS","cos","模拟量","读写","0.001","0.0","0.0","0","512","0","0","4","5034","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","28","0","0"]
["阳光逆变器","F","f","模拟量","读写","0.1","0.0","0.0","0","512","0","0","4","5035","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","32","0","0"]
["阳光逆变器","Status","status","模拟量","读写","1.0","0.0","0.0","0","512","0","0","4","5037","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","Ipv1","iPV1","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5011","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","1344","0","1"]
["阳光逆变器","Ipv2","iPV2","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5013","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","2345","0","2"]
["阳光逆变器","Ipv3","iPV3","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5015","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","3346","0","3"]
["阳光逆变器","Ipv4","iPV4","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5115","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","4347","0","4"]
["阳光逆变器","Ipv5","iPV5","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5117","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","5348","0","5"]
["阳光逆变器","Ipv6","iPV6","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5119","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","6349","0","6"]
["阳光逆变器","Ipv7","iPV7","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5121","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","7507","0","7"]
["阳光逆变器","Ipv8","iPV8","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5123","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","8508","0","8"]
["阳光逆变器","Ipv9","iPV9","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5130","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","9615","0","9"]
["阳光逆变器","Ipv10","iPV10","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5132","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","10616","0","10"]
["阳光逆变器","Ipv11","iPV11","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5134","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","11617","0","11"]
["阳光逆变器","Ipv12","iPV12","模拟量","只读","0.1","0.0","0.0","0","512","0","3","4","5136","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","60","0.5","1","12618","0","12"]
["阳光逆变器","Upv1","uPV1","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5010","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","1350","0","1"]
["阳光逆变器","Upv2","uPV2","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5012","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","2351","0","2"]
["阳光逆变器","Upv3","uPV3","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5014","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","3352","0","3"]
["阳光逆变器","Upv4","uPV4","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5114","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","4353","0","4"]
["阳光逆变器","Upv5","uPV5","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5116","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","5354","0","5"]
["阳光逆变器","Upv6","uPV6","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5118","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","6355","0","6"]
["阳光逆变器","Upv7","uPV7","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5120","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","7513","0","7"]
["阳光逆变器","Upv8","uPV8","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5122","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","8514","0","8"]
["阳光逆变器","Upv9","uPV9","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5129","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","9627","0","9"]
["阳光逆变器","Upv10","uPV10","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5131","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","10628","0","10"]
["阳光逆变器","Upv11","uPV11","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5133","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","11629","0","11"]
["阳光逆变器","Upv12","uPV12","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","5135","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","12630","0","12"]
["阳光逆变器","YX1","电网过压","开关量","只读","1.0","0.0","0.0","1","2","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100008","0","0"]
["阳光逆变器","YX2","电网过压","开关量","只读","1.0","0.0","0.0","1","3","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","-1"]
["阳光逆变器","YX3","电网欠压","开关量","只读","1.0","0.0","0.0","1","4","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100007","0","0"]
["阳光逆变器","YX4","电网欠压","开关量","只读","1.0","0.0","0.0","1","5","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX5","硬件故障","开关量","只读","1.0","0.0","0.0","1","6","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX6","电网过频","开关量","只读","1.0","0.0","0.0","1","8","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100011","0","0"]
["阳光逆变器","YX7","电网欠频","开关量","只读","1.0","0.0","0.0","1","9","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100012","0","0"]
["阳光逆变器","YX8","孤岛","开关量","只读","1.0","0.0","0.0","1","10","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100006","0","0"]
["阳光逆变器","YX9","直流分量超标","开关量","只读","1.0","0.0","0.0","1","11","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100269","0","0"]
["阳光逆变器","YX10","漏电流超标","开关量","只读","1.0","0.0","0.0","1","12","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100259","0","0"]
["阳光逆变器","YX11","电网异常","开关量","只读","1.0","0.0","0.0","1","13","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX12","电网过压","开关量","只读","1.0","0.0","0.0","1","14","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","-1"]
["阳光逆变器","YX13","电网过压","开关量","只读","1.0","0.0","0.0","1","15","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX14","PV 组件过载","开关量","只读","1.0","0.0","0.0","1","16","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100003","0","0"]
["阳光逆变器","YX15","电网电压不平衡","开关量","只读","1.0","0.0","0.0","1","17","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100010","0","0"]
["阳光逆变器","YX16","母线电压高","开关量","只读","1.0","0.0","0.0","1","19","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","-1"]
["阳光逆变器","YX17","母线电压高","开关量","只读","1.0","0.0","0.0","1","20","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX18","过流保护","开关量","只读","1.0","0.0","0.0","1","21","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX19","过流保护","开关量","只读","1.0","0.0","0.0","1","22","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX20","光伏输入配置在逆变器运行时改变","开关量","只读","1.0","0.0","0.0","1","23","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX21","母线电压不平衡","开关量","只读","1.0","0.0","0.0","1","24","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100010","0","0"]
["阳光逆变器","YX22","母线电压不平衡","开关量","只读","1.0","0.0","0.0","1","25","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX23","母线电压不平衡","开关量","只读","1.0","0.0","0.0","1","26","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX24","模块温度过高","开关量","只读","1.0","0.0","0.0","1","36","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100019","0","0"]
["阳光逆变器","YX25","环境温度过高","开关量","只读","1.0","0.0","0.0","1","37","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX26","继电器故障","开关量","只读","1.0","0.0","0.0","1","38","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX27","系统绝缘阻抗低","开关量","只读","1.0","0.0","0.0","1","39","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100018","0","0"]
["阳光逆变器","YX28","过流保护","开关量","只读","1.0","0.0","0.0","1","40","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX29","硬件故障","开关量","只读","1.0","0.0","0.0","1","41","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX30","硬件故障","开关量","只读","1.0","0.0","0.0","1","42","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX31","环境温度低","开关量","只读","1.0","0.0","0.0","1","43","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX32","交直流逆变电路故障","开关量","只读","1.0","0.0","0.0","1","44","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX33","光伏输入配置模式设置与实际连接不符","开关量","只读","1.0","0.0","0.0","1","47","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX34","硬件故障","开关量","只读","1.0","0.0","0.0","1","48","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX35","硬件故障","开关量","只读","1.0","0.0","0.0","1","49","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX36","硬件故障","开关量","只读","1.0","0.0","0.0","1","50","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX37","硬件过压过流保护","开关量","只读","1.0","0.0","0.0","1","51","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX38","风扇故障","开关量","只读","1.0","0.0","0.0","1","70","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX39","交流侧SPD告警","开关量","只读","1.0","0.0","0.0","1","71","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX40","直流侧SPD告警","开关量","只读","1.0","0.0","0.0","1","72","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX41","通讯故障","开关量","只读","1.0","0.0","0.0","1","74","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX42","光照不足","开关量","只读","1.0","0.0","0.0","1","75","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX43","PV过载","开关量","只读","1.0","0.0","0.0","1","76","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX44","PV1异常告警","开关量","只读","1.0","0.0","0.0","1","78","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX45","PV2异常告警","开关量","只读","1.0","0.0","0.0","1","79","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX46","PV3异常告警","开关量","只读","1.0","0.0","0.0","1","80","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX47","PV4异常告警","开关量","只读","1.0","0.0","0.0","1","81","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX48","AFD模块异常告警","开关量","只读","1.0","0.0","0.0","1","87","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX49","电弧故障","开关量","只读","1.0","0.0","0.0","1","88","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX50","AFD关闭告警","开关量","只读","1.0","0.0","0.0","1","89","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX51","组串1反接告警","开关量","只读","1.0","0.0","0.0","1","532","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX52","组串2反接告警","开关量","只读","1.0","0.0","0.0","1","533","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX53","组串3反接告警","开关量","只读","1.0","0.0","0.0","1","534","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX54","组串4反接告警","开关量","只读","1.0","0.0","0.0","1","535","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX55","组串5反接告警","开关量","只读","1.0","0.0","0.0","1","536","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX56","组串6反接告警","开关量","只读","1.0","0.0","0.0","1","537","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX57","组串7反接告警","开关量","只读","1.0","0.0","0.0","1","538","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX58","组串8反接告警","开关量","只读","1.0","0.0","0.0","1","539","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX59","组串9反接告警","开关量","只读","1.0","0.0","0.0","1","540","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX60","组串10反接告警","开关量","只读","1.0","0.0","0.0","1","541","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX61","组串11反接告警","开关量","只读","1.0","0.0","0.0","1","542","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX62","组串12反接告警","开关量","只读","1.0","0.0","0.0","1","543","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX63","组串13反接告警","开关量","只读","1.0","0.0","0.0","1","544","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX64","组串14反接告警","开关量","只读","1.0","0.0","0.0","1","545","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX65","组串15反接告警","开关量","只读","1.0","0.0","0.0","1","546","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX66","组串16反接告警","开关量","只读","1.0","0.0","0.0","1","547","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX67","组串1组件异常告警","开关量","只读","1.0","0.0","0.0","1","548","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX68","组串2组件异常告警","开关量","只读","1.0","0.0","0.0","1","549","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX69","组串3组件异常告警","开关量","只读","1.0","0.0","0.0","1","550","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX70","组串4组件异常告警","开关量","只读","1.0","0.0","0.0","1","551","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX71","组串5组件异常告警","开关量","只读","1.0","0.0","0.0","1","552","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX72","组串6组件异常告警","开关量","只读","1.0","0.0","0.0","1","553","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX73","组串7组件异常告警","开关量","只读","1.0","0.0","0.0","1","554","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX74","组串8组件异常告警","开关量","只读","1.0","0.0","0.0","1","555","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX75","组串9组件异常告警","开关量","只读","1.0","0.0","0.0","1","556","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX76","组串10组件异常告警","开关量","只读","1.0","0.0","0.0","1","557","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX77","组串11组件异常告警","开关量","只读","1.0","0.0","0.0","1","558","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX78","组串12组件异常告警","开关量","只读","1.0","0.0","0.0","1","559","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX79","组串13组件异常告警","开关量","只读","1.0","0.0","0.0","1","560","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","-1"]
["阳光逆变器","YX80","组串14组件异常告警","开关量","只读","1.0","0.0","0.0","1","561","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX81","组串15组件异常告警","开关量","只读","1.0","0.0","0.0","1","562","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX82","组串16组件异常告警","开关量","只读","1.0","0.0","0.0","1","563","1","2","4","5044","16位无符号","12","0","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","-1"]
["阳光逆变器","YX83","运行","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","0","0","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX84","停机","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","1","1","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX85","按键关机","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","3","3","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX86","紧急停机","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","5","5","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX87","待机","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","4","4","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX88","初始待机","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","2","2","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX89","启动中","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","6","6","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX90","告警运行","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","10","10","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX91","降额运行","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","11","11","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","1","100266","0","0"]
["阳光逆变器","YX92","调度运行","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","12","12","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX93","故障运行","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","9","9","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]
["阳光逆变器","YX94","通信故障","开关量","只读","1.0","0.0","0.0","0","512","0","4","4","5080","16位无符号","12","1","13","13","1","1","0","0","0","0","100.0","100.0","10.0","10.0","高高报警","高报警","低报警","低低报警","0.0","0","开关变位","通知","0","60","0.5","0","-1","0","1"]